## Measured Values (Server)
Object Name | Object-Type | Property Type | Object name | Unit | BACnet Object Instance | Referenced Varaible Type | Access type | COV Increment | Min. Value | Max. Value | Invalid Value | Comment
Actual Values
BAC_SupplyAirTempSensor | AI | 85 - PresentValue | BAC_SupplyAirTempSensor | °C | 1 | REAL | ReadCOV_NoWrite | 0.1 |  |  | -999.9 | Actual value of the supply air temperature
BAC_SupplyAirHumiditySensor | AI | 85 - PresentValue | BAC_SupplyAirHumiditySensor | % | 2 | REAL | ReadCOV_NoWrite | 0.1 | 0 | 100 | -999.9 | Actual value of the relative supply air humidity
BAC_SupplyAirVolFlowSensor | AI | 85 - PresentValue | BAC_SupplyAirVolFlowSensor | m3/h | 3 | REAL | ReadCOV_NoWrite | 1 |  |  |  | Actual value of the supply air volume flow
BAC_SupplyAirDuctPressSensor | AI | 85 - PresentValue | BAC_SupplyAirDuctPressSensor | Pa | 6 | REAL | ReadCOV_NoWrite | 1 |  |  | -999.9 | Actual value of the supply air duct pressure
BAC_ExtractAirTempSensor | AI | 85 - PresentValue | BAC_ExtractAirTempSensor | °C | 7 | REAL | ReadCOV_NoWrite | 0.1 |  |  | -999.9 | Actual value of extract air temperature
BAC_ExtractAirHumiditySensor | AI | 85 - PresentValue | BAC_ExtractAirHumiditySensor | % | 8 | REAL | ReadCOV_NoWrite | 1 | 0 | 100 | -999.9 | Actual value of the relative extract air humidity
BAC_ExtractAirVolFlowSensor | AI | 85 - PresentValue | BAC_ExtractAirVolFlowSensor | m3/h | 9 | REAL | ReadCOV_NoWrite | 1 |  |  |  | Actual value of the Extract air volume flow
BAC_ExtractAirDuctPressSensor | AI | 85 - PresentValue | BAC_ExtractAirDuctPressSensor | Pa | 12 | REAL | ReadCOV_NoWrite | 1 |  |  |  | Actual value of the extract air duct pressure
BAC_ExhaustAirTempSensor | AI | 85 - PresentValue | BAC_ExhaustAirTempSensor | °C | 13 | REAL | ReadCOV_NoWrite | 0.1 |  |  |  | Actual value of the exhaust air temperature
BAC_ExhaustAirHumiditySensor | AI | 85 - PresentValue | BAC_ExhaustAirHumiditySensor | % | 14 | REAL | ReadCOV_NoWrite | 1 | 0 | 100 | -999.9 | Actual value of the relative exhaust air humidity
BAC_RoomAirTempSensor | AI | 85 - PresentValue | BAC_RoomAirTempSensor | °C | 15 | REAL | ReadCOV_NoWrite | 0.1 |  |  | -999.9 | Actual value of room air temperature
BAC_RoomAirHumiditySensor | AI | 85 - PresentValue | BAC_RoomAirHumiditySensor | % | 16 | REAL | ReadCOV_NoWrite | 1 | 0 | 100 | -999.9 | Actual value of the relative room air humidity
BAC_OutsideAirTempSensor | AI | 85 - PresentValue | BAC_OutsideAirTempSensor | °C | 17 | REAL | ReadCOV_NoWrite | 0.1 |  |  | -999.9 | Actual value of outside air temperature
BAC_OutsideAirHumiditySensor | AI | 85 - PresentValue | BAC_OutsideAirHumiditySensor | % | 18 | REAL | ReadCOV_NoWrite | 1 | 0 | 100 | -1 | Actual value of the relative outside air humidity
BAC_IndoorAirQualitySensor | AI | 85 - PresentValue | BAC_IndoorAirQualitySensor | ppm | 20 | REAL | ReadCOV_NoWrite | 1 | 0 | 10000 | -1 | Actual value of the room (indoor) air quality
BAC_SupplyAirHumidityAbs | AI | 85 - PresentValue | BAC_SupplyAirHumidityAbs | g/kg | 25 | REAL | ReadCOV_NoWrite | 0.1 | 0 | 30 | -999.9 | Actual value of the absolute supply air humidity (calculated!)
BAC_ExtractAirHumidityAbs | AI | 85 - PresentValue | BAC_ExtractAirHumidityAbs | g/kg | 26 | REAL | ReadCOV_NoWrite | 0.1 | 0 | 30 | -999.9 | Actual value of the absolute extract air humidity (calculated!)
BAC_RoomAirHumidityAbs | AI | 85 - PresentValue | BAC_RoomAirHumidityAbs | g/kg | 27 | REAL | ReadCOV_NoWrite | 0.1 | 0 | 30 | -999.9 | Actual value of the absolute room air humidity (calculated!)
BAC_OutsideAirHumidityAbs | AI | 85 - PresentValue | BAC_OutsideAirHumidityAbs | g/kg | 28 | REAL | ReadCOV_NoWrite | 0.1 | 0 | 30 | -999.9 | Actual value of the absolute outside air humidity (calculated!)
BAC_ExhaustAirHumidityAbs | AI | 85 - PresentValue | BAC_ExhaustAirHumidityAbs | g/kg | 29 | REAL | ReadCOV_NoWrite | 0.1 | 0 | 30 | -999.9 | Actual value of the absolute exhaust air humidity (calculated!)
BAC_IndoorVOCSensor | AI | 85 - PresentValue | BAC_IndoorVOCSensor | % | 30 | REAL | ReadCOV_NoWrite | 0.1 | 0 | 100 | -999.9 | Actual value of the room (indoor) Volatile Organic Compounds (VOC) sensor
Note on A1: Thielert, Udo: Same object name means the same object but another property.

## Set points (Server)
Object Name | Object-Type | Property Type | Unit | BACnet Object Instance | Referenced Varaible Type | Access type | COV Increment | Min. Value | Max. Value | Invalid Value | Comment
Set points
BAC_SupplyAirTempSetp | AV | 85 - PresentValue | °C | 33 | REAL | ReadCOV_Commandable | 0.1 |  |  | -999.9 | Set point supply air temperature
BAC_ExtractAirTempSetp | AV | 85 - PresentValue | °C | 34 | REAL | ReadCOV_Commandable | 0.1 |  |  | -999.9 | Set point extract air temperature
BAC_RoomAirTempSetp | AV | 85 - PresentValue | °C | 35 | REAL | ReadCOV_Commandable | 0.1 |  |  | -999.9 | Set point room air temperature
BAC_SupplyAirPressureSetp | AV | 85 - PresentValue | Pa | 36 | REAL | ReadCOV_Commandable | 1 |  |  | -999.9 | Set point supply air duct pressure
BAC_ExtractAirPressureSetp | AV | 85 - PresentValue | Pa | 37 | REAL | ReadCOV_Commandable | 1 |  |  | -999.9 | Set point extract air duct pressure
BAC_SupplyAirVolumeFlowSetp | AV | 85 - PresentValue | m3/h | 38 | REAL | ReadCOV_Commandable | 1 |  |  | -999.9 | Set point supply air volume flow rate
BAC_ExtractAirVolumeFlowSetp | AV | 85 - PresentValue | m3/h | 39 | REAL | ReadCOV_Commandable | 1 |  |  | -999.9 | Set point extract air volume flow rate
BAC_SupplyAirFanSpeedSetp | AV | 85 - PresentValue | % | 40 | REAL | ReadCOV_Commandable | 1 |  |  | -999.9 | Set point supply air fan speed
BAC_ExtractAirFanSpeedSetp | AV | 85 - PresentValue | % | 41 | REAL | ReadCOV_Commandable | 1 |  |  | -999.9 | Set point extract air fan speed
BAC_AirQualityThreshold_Per | AV | 85 - PresentValue | % | 42 | REAL | ReadCOV_Commandable | 0.1 |  |  | -999.9 | Air quality threshold in precent
BAC_AirQualityThreshold_ppm | AV | 85 - PresentValue | ppm | 43 | REAL | ReadCOV_Commandable | 1 |  |  | -999.9 | Air quality threshold in ppm
BAC_MixedAirDamperPosSetp | AV | 85 - PresentValue | % | 44 | REAL | ReadCOV_Commandable | 1 |  |  | -999.9 | Set point mixed air damper position
BAC_OffsetRoomAirCoolSetP | AV | 85 - PresentValue | K | 46 | REAL | ReadCOV_Commandable | 0.1 | 0 | 10 | -999.9 | Rom air heating set point - Offset = the cooling set point
BAC_OffsetExtractAirCoolSetP | AV | 85 - PresentValue | K | 47 | REAL | ReadCOV_Commandable | 0.1 | 0 | 10 | -999.9 | Extract air heating set point - Offset = the cooling set point
BAC_ExtractAirHumidityRelSetp | AV | 85 - PresentValue | % | 48 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Set point extract air humidity relative
BAC_ExtractAirHumidityAbsSetp | AV | 85 - PresentValue | g/kg | 49 | REAL | ReadCOV_Commandable | 0.1 | 0 | 30 | -999.9 | Set point extract air humidity absolute
BAC_IndoorHumidityRelSetp | AV | 85 - PresentValue | % | 50 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Set point indoor air humidity relative
BAC_IndoorHumidityAbsSetp | AV | 85 - PresentValue | g/kg | 51 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Set point indoor air humidity absolute
BAC_IndoorDehumidityRelSetp | AV | 85 - PresentValue | % | 52 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Set point indoor air dehumidity relative
BAC_IndoorDehumidityAbsSetp | AV | 85 - PresentValue | g/kg | 53 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Set point indoor air dehumidity absolute
BAC_SupplyAirHumidityRelSetp | AV | 85 - PresentValue | % | 54 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Set point supply air humidity relative
BAC_SupplyAirHumidityAbsSetp | AV | 85 - PresentValue | g/kg | 55 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Set point supply air humidity absolute
BAC_OutdoorAirPortionSetp | AV | 85 - PresentValue | % | 90 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Set point outdoor air portion (mixed air damper controlled)
BAC_MinOutdoorAirAmountSetp | AV | 85 - PresentValue | % | 91 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Set point min outdoor air amount
BAC_ExtractDehumidityRelHyst | AV | 85 - PresentValue | % | 108 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Extract air dehumidity hysteresis relative
BAC_ExtractDehumidityAbsHyst | AV | 85 - PresentValue | g/kg | 109 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Extract air dehumidity hysteresis absolute
BAC_SupplyAirTempBaseSp | AV | 85 - PresentValue | °C | 110 | REAL | ReadCOV_Commandable | 0.1 |  |  | -999.9 | Supply air temperature base set point
BAC_ExtractAirTempBaseSp | AV | 85 - PresentValue | °C | 111 | REAL | ReadCOV_Commandable | 0.1 |  |  | -999.9 | Extract air temperature base set point
BAC_IndoorAirTempBaseSp | AV | 85 - PresentValue | °C | 112 | REAL | ReadCOV_Commandable | 0.1 |  |  | -999.9 | Indoor air temperature base set point
BAC_OperationMode | MV | 85 - PresentValue | -- | 1 | UDINT | ReadCOV_Commandable | 1 | 1 | 6 |  | Operation Modes:1=Device off; 2=Scheduler;3=User Profile 1; 4=User Profile 2; 5=User Profile 3; 6=User Profile 4
BAC_ControlType | MV | 85 - PresentValue | -- | 2 | UDINT | ReadCOV_Commandable | 1 | 1 | 7 |  | Temperature Control Types: 1=none; 2=Extract Air Temperature; 3=Supply Air Temperature; 4=Extract Air Cascade; 5=Outside Air Temp. Curve; 6=Room Air Temperature; 7=Room Air Cascade
BAC_SupplyAirFanMode | MV | 85 - PresentValue | -- | 3 | UDINT | ReadCOV_Commandable | 1 | 1 | 10 |  | Supply air fan mode -- 1=Off (Temperatur controlled); 2=Off (Manual controlled); 3=Automatic; 4=Automatic Mute; 5=Stage 1; 6=Stage 2; 7=Stage 3; 8=Stage 4; 9=Stage 5; 10=Manual Supply Air Fan Speed (Should set in BACnet Object BAC_SupplyAirFanSpeedSetp)
BAC_ExtractAirFanMode | MV | 85 - PresentValue | -- | 4 | UDINT | ReadCOV_Commandable | 1 | 1 | 10 |  | Extract air fan mode -- 1=Off (Temperatur controlled); 2=Off (Manual controlled); 3=Automatic; 4=Automatic Mute; 5=Stage 1; 6=Stage 2; 7=Stage 3; 8=Stage 4; 9=Stage 5; 10=Manual Extract Air Fan Speed (Should set in Bacnet Object BAC_ExtractAirFanSpeedSetp)
BAC_ControlMode | MV | 85 - PresentValue | -- | 5 | UDINT | ReadCOV_Commandable | 1 | 0 | 4 |  | Temperature control mode: 1 = Fan only; 2 = Passive Operation (Night Purge); 3 = Automatic; 4 = Heating only; 5 = Cooling only
BAC_HumidityCtrlType | MV | 85 - PresentValue | -- | 6 | UDINT | ReadCOV_Commandable | 1 | 1 | 6 |  | Humidify Control Types: 1= None; 2=Extract Air; 3=Supply Air; 4=Cascade Extract Air; 5= Indoor Air; 6=Cascade Indoor Air
BAC_HumidityCtrlMode | MV | 85 - PresentValue | -- | 7 | UDINT | ReadCOV_Commandable | 1 | 1 | 4 |  | Humidify Control Modes: 1=None; 2=Humidify; 3=Dehumidify; 4=Automatic
BAC_MasterSchedulerState | MV | 85 - PresentValue | -- | 9 | UDINT | ReadCOV_Commandable | 1 | 1 | 4 |  | Only for reading. Master scheduler output state :1=Device off; 3=User Profile 1; 4=User Profile 2; 5=User Profile 3; 6=User Profile 4.
Note on A1: Thielert, Udo: Same object name means the same object but another property.

## Alarms (Server)
Object Name | Object-Type | Property Type | Property Variable | Unit | BACnet Object Instance | Referenced Varaible Type | Access type | COV Increment | Min. Value | Max. Value | Invalid Value | Comment
Alarms
BAC_AckAllAlarms | BV | 85 - PresentValue | BAC_AckAllAlarms | -- | 1 | BOOL | ReadCOV_Commandable |  |  |  | FALSE | Reset all active alarms on the controller
BAC_AlarmUrgent | BV | 85 - PresentValue | BAC_AlarmUrgent | -- | 2 | BOOL | Read_NoWrite |  |  |  |  | Urgently aggregate alarm message
BAC_AlarmNotUrgent | BV | 85 - PresentValue | BAC_AlarmNotUrgent | -- | 3 | BOOL | Read_NoWrite |  |  |  |  | Aggregate alarm message
BAC_MaintenanceNotification | BV | 85 - PresentValue | BAC_MaintenanceNotificationfication | -- | 4 | BOOL | Read_NoWrite |  |  |  |  | Maintenance needed
BAC_AlarmFire | BV | 85 - PresentValue | BAC_AlarmFire | -- | 5 | BOOL | Read_NoWrite
BAC_AlarmSmoke | BV | 85 - PresentValue | BAC_AlarmSmoke | -- | 6 | BOOL | Read_NoWrite
BAC_AlarmWarmUp | BV | 85 - PresentValue | BAC_AlarmWarmUp | -- | 7 | BOOL | Read_NoWrite
BAC_AlarmFrostProtectionAir | BV | 85 - PresentValue | BAC_AlarmFrostProtectionAir | -- | 8 | BOOL | Read_NoWrite
BAC_AlarmSupplyAirTempSensor | BV | 85 - PresentValue | BAC_AlarmSupplyAirTempSensor | -- | 9 | BOOL | Read_NoWrite
BAC_AlarmSupplyAirHumiditySensor | BV | 85 - PresentValue | BAC_AlarmSupplyAirHumiditySensor | -- | 10 | BOOL | Read_NoWrite
BAC_AlarmExtractAirTempSensor | BV | 85 - PresentValue | BAC_AlarmExtractAirTempSensor | -- | 11 | BOOL | Read_NoWrite
BAC_AlarmExtractAirHumiditySensor | BV | 85 - PresentValue | BAC_AlarmExtractAirHumiditySensor | -- | 12 | BOOL | Read_NoWrite
BAC_AlarmOutsideAirTempSensor | BV | 85 - PresentValue | BAC_AlarmOutsideAirTempSensor | -- | 13 | BOOL | Read_NoWrite
BAC_AlarmOutsideAirHumiditySensor | BV | 85 - PresentValue | BAC_AlarmOutsideAirHumiditySensor | -- | 14 | BOOL | Read_NoWrite
BAC_AlarmRoomAirTempSensor | BV | 85 - PresentValue | BAC_AlarmRoomAirTempSensor | -- | 15 | BOOL | Read_NoWrite
BAC_AlarmRoomAirHumiditySensor | BV | 85 - PresentValue | BAC_AlarmRoomAirHumiditySensor | -- | 16 | BOOL | Read_NoWrite
BAC_AlarmExhaustAirTempSensor | BV | 85 - PresentValue | BAC_AlarmExhaustAirTempSensor | -- | 17 | BOOL | Read_NoWrite
BAC_AlarmExhaustAirHumiditySensor | BV | 85 - PresentValue | BAC_AlarmExhaustAirHumiditySensor | -- | 18 | BOOL | Read_NoWrite
BAC_AlarmAirQualitySensor | BV | 85 - PresentValue | BAC_AlarmAirQualitySensor | -- | 19 | BOOL | Read_NoWrite
BAC_AlarmAirQualityThresholdOvershoot | BV | 85 - PresentValue | BAC_AlarmAirQualityThresholdOvershoot | -- | 20 | BOOL | Read_NoWrite
BAC_AlarmSupplyAirFiltPressSensor | BV | 85 - PresentValue | BAC_AlarmSupplyAirFiltPressSensor | -- | 21 | BOOL | Read_NoWrite
BAC_AlarmExtractAirFiltPressSensor | BV | 85 - PresentValue | BAC_AlarmExtractAirFiltPressSensor | -- | 22 | BOOL | Read_NoWrite
BAC_AlarmOutsideAirFiltPressSensor | BV | 85 - PresentValue | BAC_AlarmOutsideAirFiltPressSensor | -- | 23 | BOOL | Read_NoWrite
BAC_MaintenanceSupplyAirFilter | BV | 85 - PresentValue | BAC_MaintanceSupplyAirFilter | -- | 24 | BOOL | Read_NoWrite
BAC_MaintenanceExtractAirFilter | BV | 85 - PresentValue | BAC_MaintanceExtractAirFilter | -- | 25 | BOOL | Read_NoWrite
BAC_MaintenanceOutsideAirFilter | BV | 85 - PresentValue | BAC_MaintanceOutsideAirFilter | -- | 26 | BOOL | Read_NoWrite
BAC_AlarmSupplyAirNozzelPressSensor | BV | 85 - PresentValue | BAC_AlarmSupplyAirNozzelPressSensor | -- | 27 | BOOL | Read_NoWrite
BAC_AlarmExtractAirNozzelPressSensor | BV | 85 - PresentValue | BAC_AlarmExtractAirNozzelPressSensor | -- | 28 | BOOL | Read_NoWrite
BAC_AlarmHeaterPump | BV | 85 - PresentValue | BAC_AlarmHeaterPump | -- | 29 | BOOL | Read_NoWrite
BAC_MaintenanceHeaterPump | BV | 85 - PresentValue | BAC_MaintenanceHeaterPump | -- | 30 | BOOL | Read_NoWrite
BAC_AlarmCoolerPump | BV | 85 - PresentValue | BAC_AlarmCoolerPump | -- | 31 | BOOL | Read_NoWrite
BAC_MaintenanceCoolerPump | BV | 85 - PresentValue | BAC_MaintenanceCoolerPump | -- | 32 | BOOL | Read_NoWrite
BAC_MaintenanceMotorECOROT | BV | 85 - PresentValue | BAC_MaintenanceMotorECOROT | -- | 33 | BOOL | Read_NoWrite
BAC_AlarmMotorECOROT | BV | 85 - PresentValue | BAC_AlarmMotorECOROT | -- | 34 | BOOL | Read_NoWrite
BAC_MaintenancePumpECOFLOW | BV | 85 - PresentValue | BAC_MaintenancePumpECOFLOW | -- | 35 | BOOL | Read_NoWrite
BAC_AlarmPumpECOFLOW | BV | 85 - PresentValue | BAC_AlarmPumpECOFLOW | -- | 36 | BOOL | Read_NoWrite
BAC_AlarmIcingSensor | BV | 85 - PresentValue | BAC_AlarmIcingSensor | -- | 37 | BOOL | Read_NoWrite
BAC_AlarmCoolerValve | BV | 85 - PresentValue | BAC_AlarmCoolerValve | -- | 38 | BOOL | Read_NoWrite
BAC_AlarmHeaterValve | BV | 85 - PresentValue | BAC_AlarmHeaterValve | -- | 39 | BOOL | Read_NoWrite
BAC_AlarmPumpECOFLOW_Ti | BV | 85 - PresentValue | BAC_AlarmPumpECOFLOW_Ti | -- | 40 | BOOL | Read_NoWrite
BAC_AlarmChangeOverTempInvalid | BV | 85 - PresentValue | BAC_AlarmChangeOverTempInvalid | -- | 41 | BOOL | Read_NoWrite
BAC_AlarmERSAntiIcingTemp | BV | 85 - PresentValue | BAC_AlarmERSAntiIcingTemp | -- | 42 | BOOL | Read_NoWrite
BAC_AlarmERSAntiIcingProtection | BV | 85 - PresentValue | BAC_AlarmERSAntiIcingProtection | -- | 43 | BOOL | Read_NoWrite
BAC_AlarmInvalidOutsideTemp | BV | 85 - PresentValue | BAC_AlarmInvalidOutsideTemp | -- | 44 | BOOL | Read_NoWrite
BAC_AlarmSupplyAirFan | BV | 85 - PresentValue | BAC_AlarmSupplyAirFan | -- | 45 | BOOL | Read_NoWrite
BAC_AlarmExtractAirFan | BV | 85 - PresentValue | BAC_AlarmExtractAirFan | -- | 46 | BOOL | Read_NoWrite
BAC_AlarmInverterMitsubishi1 | BV | 85 - PresentValue | BAC_AlarmInverterMitsubishi1 | -- | 47 | BOOL | Read_NoWrite
BAC_MaintenanceInverterMitsubishi1 | BV | 85 - PresentValue | BAC_MaintenanceInverterMitsubishi1 | -- | 48 | BOOL | Read_NoWrite
BAC_AlarmInverterMitsubishi2 | BV | 85 - PresentValue | BAC_AlarmInverterMitsubishi2 | -- | 49 | BOOL | Read_NoWrite
BAC_MaintenanceInverterMitsubishi2 | BV | 85 - PresentValue | BAC_MaintenanceInverterMitsubishi2 | -- | 50 | BOOL | Read_NoWrite
BAC_AlarmInverterDaikin1 | BV | 85 - PresentValue | BAC_AlarmInverterDaikin1 | -- | 51 | BOOL | Read_NoWrite
BAC_MaintenanceInverterDaikin1 | BV | 85 - PresentValue | BAC_MaintenanceInverterDaikin1 | -- | 52 | BOOL | Read_NoWrite
BAC_AlarmInverterDaikin2 | BV | 85 - PresentValue | BAC_AlarmInverterDaikin2 | -- | 53 | BOOL | Read_NoWrite
BAC_MaintenanceInverterDaikin2 | BV | 85 - PresentValue | BAC_MaintenanceInverterDaikin2 | -- | 54 | BOOL | Read_NoWrite
BAC_TrippingAlarmSupplyAirFan | BV | 85 - PresentValue | BAC_TrippingAlarmSupplyAirFan | -- | 55 | BOOL | Read_NoWrite
BAC_TrippingAlarmExtractAirFan | BV | 85 - PresentValue | BAC_TrippingAlarmExtractAirFan | -- | 56 | BOOL | Read_NoWrite
BAC_AlarmFrostProtectionEvaporator | BV | 85 - PresentValue | BAC_AlarmFrostProtectionEvaporator | -- | 57 | BOOL | Read_NoWrite
BAC_AlarmCondensingStage1 | BV | 85 - PresentValue | BAC_AlarmCondensingStage1 | -- | 58 | BOOL | Read_NoWrite
BAC_MaintenanceCondensingStage1 | BV | 85 - PresentValue | BAC_MaintenanceCondensingStage1 | -- | 59 | BOOL | Read_NoWrite
BAC_AlarmCondensingStage2 | BV | 85 - PresentValue | BAC_AlarmCondensingStage2 | -- | 60 | BOOL | Read_NoWrite
BAC_MaintenanceCondensingStage2 | BV | 85 - PresentValue | BAC_MaintenanceCondensingStage2 | -- | 61 | BOOL | Read_NoWrite
BAC_AlarmRoomFrostProtection | BV | 85 - PresentValue | BAC_AlarmRoomFrostProtection | -- | 62 | BOOL | Read_NoWrite |  |  |  |  | Missing sensor
iBN_AlarmUrgentNode1.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode1.Trigger | -- | 100 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode1.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode1.Trigger | -- | 101 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode1.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode1.Trigger | -- | 102 | BOOL | Read_Writeable
iBN_AlarmUrgentNode2.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode2.Trigger | -- | 103 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode2.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode2.Trigger | -- | 104 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode2.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode2.Trigger | -- | 105 | BOOL | Read_Writeable
iBN_AlarmUrgentNode3.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode3.Trigger | -- | 106 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode3.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode3.Trigger | -- | 107 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode3.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode3.Trigger | -- | 108 | BOOL | Read_Writeable
iBN_AlarmUrgentNode4.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode4.Trigger | -- | 109 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode4.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode4.Trigger | -- | 110 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode4.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode4.Trigger | -- | 111 | BOOL | Read_Writeable
iBN_AlarmUrgentNode5.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode5.Trigger | -- | 112 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode5.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode5.Trigger | -- | 113 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode5.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode5.Trigger | -- | 114 | BOOL | Read_Writeable
iBN_AlarmUrgentNode6.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode6.Trigger | -- | 115 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode6.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode6.Trigger | -- | 116 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode6.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode6.Trigger | -- | 117 | BOOL | Read_Writeable
iBN_AlarmUrgentNode7.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode7.Trigger | -- | 118 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode7.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode7.Trigger | -- | 119 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode7.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode7.Trigger | -- | 120 | BOOL | Read_Writeable
iBN_AlarmUrgentNode8.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode8.Trigger | -- | 121 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode8.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode8.Trigger | -- | 122 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode8.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode8.Trigger | -- | 123 | BOOL | Read_Writeable
iBN_AlarmUrgentNode9.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode9.Trigger | -- | 124 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode9.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode9.Trigger | -- | 125 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode9.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode9.Trigger | -- | 126 | BOOL | Read_Writeable
iBN_AlarmUrgentNode10.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode10.Trigger | -- | 127 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode10.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode10.Trigger | -- | 128 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode10.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode10.Trigger | -- | 129 | BOOL | Read_Writeable
iBN_AlarmUrgentNode11.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode11.Trigger | -- | 130 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode11.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode11.Trigger | -- | 131 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode11.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode11.Trigger | -- | 132 | BOOL | Read_Writeable
iBN_AlarmUrgentNode12.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode12.Trigger | -- | 133 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode12.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode12.Trigger | -- | 134 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode12.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode12.Trigger | -- | 135 | BOOL | Read_Writeable
iBN_AlarmUrgentNode13.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode13.Trigger | -- | 136 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode13.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode13.Trigger | -- | 137 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode13.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode13.Trigger | -- | 138 | BOOL | Read_Writeable
iBN_AlarmUrgentNode14.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode14.Trigger | -- | 139 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode14.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode14.Trigger | -- | 140 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode14.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode14.Trigger | -- | 141 | BOOL | Read_Writeable
iBN_AlarmUrgentNode15.Trigger | BV | 85 - PresentValue | iBN_AlarmUrgentNode15.Trigger | -- | 142 | BOOL | Read_Writeable
iBN_AlarmNotUrgentNode15.Trigger | BV | 85 - PresentValue | iBN_AlarmNotUrgentNode15.Trigger | -- | 143 | BOOL | Read_Writeable
iBN_MaintenanceNotificationNode15.Trigger | BV | 85 - PresentValue | iBN_MaintenanceNotificationNode15.Trigger | -- | 144 | BOOL | Read_Writeable
Note on A1: Thielert, Udo: Same object name means the same object but another property.

## Actuator states (Server)
Object Name | Object-Type | Property Type | Unit | BACnet Object Instance | Referenced Varaible Type | Access type | COV Increment | Min. Value | Max. Value | Invalid Value | Comment
Analog Actuator States
BAC_ExhaustAirDamperPos | AO | 85 - PresentValue | % | 1 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual position of the exhaust air damper
BAC_OutsideAirDamperPos | AO | 85 - PresentValue | % | 2 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual position of the outside air damper
BAC_MixedAirDamperPos | AO | 85 - PresentValue | % | 3 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual position of the mixed air damper
BAC_ValveHeaterPos | AO | 85 - PresentValue | % | 4 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual position of the heater valve
BAC_EHeaterPowerOut | AO | 85 - PresentValue | % | 5 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual e-heater output
BAC_ValveCoolerPos | AO | 85 - PresentValue | % | 6 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual position of the cooler valve
BAC_ERSOutput | AO | 85 - PresentValue | % | 7 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual output of the energy recovery system
BAC_CondHeatingReq | AO | 85 - PresentValue | % | 8 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual output of the condenser unit (heating)
BAC_CondCoolingReq | AO | 85 - PresentValue | % | 9 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual output of the condenser unit (cooling)
BAC_SupplyAirFanSpeed | AO | 85 - PresentValue | % | 10 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual supply air fan speed
BAC_ExtractAirFanSpeed | AO | 85 - PresentValue | % | 11 | REAL | ReadCOV_Commandable | 0.1 | 0 | 100 | -999.9 | Actual extract air fan speed
Digital Actuator States as a digital outputs
BAC_HeaterPumpIsOn | BO | 85 - PresentValue |  | 1 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary output:If 1 then the heater pump is on
BAC_CoolerPumpIsOn | BO | 85 - PresentValue |  | 2 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary output:If 1 then the cooler pump is on
BAC_EcorotIsOn | BO | 85 - PresentValue |  | 3 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary output:If 1 then the ERS ECOROT is on
BAC_EcoflowISOn | BO | 85 - PresentValue |  | 4 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary output:If 1 then the ERS ECOFLOW is on
Digital Actuator States as a digital values
BAC_SupplyAirFanIsRunning | BV | 85 - PresentValue |  | 200 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary value: If 1 then the supply air fan is running
BAC_ExtractAirFanIsRunning | BV | 85 - PresentValue |  | 201 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary value: If 1 then the extract air fan is running
BAC_UnitIsOn | BV | 85 - PresentValue |  | 202 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary value: If 1 then the unit is switched on
BAC_DefrostingIsActive | BV | 85 - PresentValue |  | 203 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary value: If 1 then is the defrosting active
BAC_HeatingIsActive | BV | 85 - PresentValue |  | 204 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary value: If 1 then heating is active
BAC_CoolingIsActive | BV | 85 - PresentValue |  | 205 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary value: If 1 then cooling is active
BAC_RequestCondUnitStage1 | BV | 85 - PresentValue |  | 206 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary value: If 1 then existing a request for the stage 1 of the external condenser
BAC_RequestCondUnitStage2 | BV | 85 - PresentValue |  | 207 | BOOL | ReadCOV_NoWrite | 1 | 0 | 1 |  | Binary value: If 1 then existing a request for the stage 2 of the external condenser
Note on A1: Thielert, Udo: Same object name means the same object but another property.

## Any other
Object Name | Object-Type | Property Type | Unit | BACnet Object Instance | Referenced Varaible Type | Access type | COV Increment | Min. Value | Max. Value | Invalid Value | Comment
Any other
FG_Scheduler | Sched | 85 - PresentValue | -- | 1 | INT | ------------- | -- | 0 | 6 | -1 | Possible Values:1=Device off; 3=User Profile 1; 4=User Profile 2; 5=User Profile 3; 6=User Profile 4
Note on A1: Thielert, Udo: Same object name means the same object but another property.